1. Size of Drainage Piping

Fittings used for drainage shall be of the drainage type, have a smooth interior waterway, and be constructed so as to allow one fourth (1/4) inch (20.9 mm/m) per    foot grade.

1.1. The minimum sizes of vertical and/or horizontal drainage piping shall be determined from the total of all fixture units connected thereto, and additionally, in the case of vertical drainage pipes, in accordance with their length.

1.2. Table 2 shows the maximum number of fixture units allowed on any vertical or horizontal drainage pipe, building drain or building sewer of a given size; the maximum number of fixture units allowed on any branch interval of a given size; and the maximum length (in feet and meters) of any vertical drainage pipe of a given size.

## TABLE 1-1  Drainage Fixture Unit Values (DFU)

|  | Min. Size Trap and Trap Arm | Private | Public |
| --- | --- | --- | --- |
| Kitchen, domestic | 1-1/2”(40mm) | 2.0 | 2.0 |

1. Trap sizes shall not be increased to the point where the fixture discharge may be inadequate to maintain their self-scouring properties.

2. Provide a 2” (51 mm) minimum drain.

## TABLE 1-2  Discharge Capacity In Gallons per Minute(Liters per Second) . For Intermittent Flow Only

| GPM | (I/sec.) |  |  |
| --- | --- | --- | --- |
| Up to 7-1/2 | (Up to 0.47) | Equals | 1 Unit |
| 8 to 15 | (0.50 to 0.95) | Equals | 2 Units |
| 16 to 30 | (1.00 to 1.89) | Equals | 4 Units |
| 31 to 50 | (1.95 to 3.15) | Equals | 6 Units |

Discharge capacity for over 50 gallons per minute(3.15 L/sec.) shall be determined by the Administrative Authority.

2. Fixture Connections (Drainage)

Two fixtures set back-to-back, or side-by-side, within the distance allowed between a trap and its vent, may be served by a single vertical drainage pipe provided that each fixture wastes separately into an approved double fixture fitting having inlet openings at the same level.

## TABLE 2  Maximum Unit Loading and Maximum Length of Drainage and Vent Piping

| Size of Pipe, inches (mm) | 1-1/4 (32) | 1-1/2 (40) | 2 (50) | 2-1/2 (65) | 3 (80) | 4 (100) | 5 (125) | 6 (150) | 8 (200) | 10 (250) | 12 (300) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ## Maximum Units Drainage Piping Vertical Horizontal | 1 1 | 2 1 | 16 8 | 32 14 | 48 35 | 256 216 | 600 428 | 1380 720 | 3600 2640 | 5600 4680 | 8400 8200 |
| ## Maximum Length Drainage Piping Vertical, feet (m) Horizontal (Unlimited) | 45 (14) | 65 (20) | 85 (26) | 148 (45) | 212 (65) | 300 (91) | 390 (119) | 510 (155) | 750 (228) |  |  |
| ## Vent Piping Horizontal and Vertical Maximum Units Maximum Lengths, feet (m) | 1 45 (14) | 8 60 (18) | 24 120 (37) | 48 180 (55) | 84 212 (65) | 256 300 (91) | 600 390 (119) | 1380 510 (155) | 3600 750 (228) |  |  |

1.  Excluding trap arm.

2.  Except sinks, urinals and dishwashers.

3.  Except six-unit traps or water closets.

4.  Only four (4) water closets or six-unit traps allowed on any vertical pipe or stack; and not to exceed three (3) water closets or six-unit traps on any horizontal branch or drain.

5.  Based on one-fourth (1/4) inch per foot (20.9 mm/m) slope. For one-eighth (1/8) inch per foot (10.4 mm/m) slope, multiply horizontal fixture units by a factor of 0.8.

Note: The diameter of an individual vent shall not be less than one and one-fourth (1-1/4) inches (31.8 mm) nor less than one-half (1/2) the diameter of the drain to which it is connected. Fixture unit load values for drainage and vent piping shall be computed from Tables 1-1 and 1-2. Not to exceed one-third (1/3) of the total permitted length of any vent may be installed in a horizontal position. When vents are increased one (1) pipe size for their entire length, the maximum length limitations specified in this table do not apply.

#### 3. Changes in Direction of Drainage Flow

3.1. Changes in direction of drainage piping shall be made by the appropriate use of approved fittings and shall be of the angles presented by a one-sixteenth (1/16) bend, one-eighth (1/8) bend, or one-sixth (1/6) bend, or other approved fittings of equivalent sweep.

3.2. Horizontal drainage lines, connecting with a vertical stack, shall enter through forty-five (45) degree (0.79 rad) wye branches, sixty (60) degree (1.05 rad) wye branches, combination wye and 1/8 bend branches, sanitary tee or sanitary tapped tee branches, or other approved fittings of equivalent sweep. No fitting having more than one (1) inlet at the same level shall be used unless such fitting is constructed so that the discharge from one (1) inlet cannot readily enter any other inlet. Double sanitary tees may be used when the barrel of the fitting is at least two (2) pipe sizes larger than the largest inlet, (pipe sizes recognized for this purpose are 2”, 2-1/2”, 3”, 3-1/2”, 4”, 4-1/2”, 5”, 6”, etc.) (50, 65, 80, 90, 100, 115, 125, 150 mm, etc.).

3.3. Horizontal drainage lines connecting with other horizontal drainage lines shall enter through forty-five (45) degree (0.79 rad) wye branches, combination wye and one-eighth (1/8) bend branches; or other approved fittings of equivalent sweep. Sixty (60) degree (1.05 rad) branches or offsets may be used only when installed in a true vertical position.

3.4. Vertical drainage lines connecting with horizontal drainage lines shall enter through forty-five (45) degree (0.79 rad) wye branches, combination wye and one-eighth (1/8) bend branches; or other approved fittings of equivalent sweep. Sixty (60) degree (1.05 rad) branches or offsets may be used only when installed in a true vertical position.

4. Cleanouts

4.1. Each horizontal drainage pipe shall be provided with a cleanout at its upper terminal and each run of piping, which is more than one hundred (100) feet (30480 mm) in total developed length, shall be provided with a cleanout for each one hundred (100) feet (30480 mm), or fraction thereof, in length of such piping.

Exceptions:

(1) Cleanouts may be omitted on a horizontal drain line less than five (5) feet (1524 mm) in length unlesuch line is serving sinks or urinals.

(2) Cleanouts may be omitted on any horizontal drainage pipe installed on a slope of seventy-two (72) degrees (1.26 rad ) or less from the vertical angle (angle of  one-fifth (1/5) bend).

(3) Excepting the building drain and its horizontal branches, a cleanout shall not be required on any pipe or piping which is above the floor level of the lowest floor of the building.

(4) An approved type of two-way cleanout fitting, installed inside the building wall near the connection between the building drain and building sewer or installed outside of a building at the lower end of a building drain and extended to grade, may be substituted for an upper terminal cleanout.

4.2.An additional cleanout shall be provided in a drainage line for each aggregate horizontal change of direction exceeding one hundred and thirty-five 135) degrees (2.36 rad).

4.3. Each cleanout shall be installed so that it opens to allow cleaning in the direction of flow of the soil or waste or at right angles thereto and, except in the case of wye branch and end-of-line cleanouts, shall be installed vertically above the flow line of the pipe.

4.4.Each cleanout extension shall be considered as drainage piping and each ninety (90) degree (1.6 rad) cleanout extension shall be extended from a wye type fitting or other approved fitting of equivalent sweep.

## TABLE 4  Cleanouts (Metric)

| Size of Pipe (mm) | Size of Cleanout (mm) | Threads per 25.4 mm |
| --- | --- | --- |
| 40 50 65 80 100 & larger | 38 38 64 64 89 | 11-1/2 11-1/2 8 8 8 |

5. Grade of Horizontal Drainage Piping

Horizontal drainage piping shall be run in practical alignment and a uniform slope of not less than one-fourth (1/4) of an inch per foot (20.9 mm/m) or two (2) percent toward the point of disposal provided that, where it is impractical due to the depth of the street sewer or to the structural features or to the arrangement of any building or structure to obtain a slope of one-fourth (1/4) of an inch per foot (20.9 mm/m) or two (2) percent, any such pipe or piping four (4) inches (100 mm) or larger in diameter may have a slope of not less than one-eighth (1/8) of an inch per foot (10.5 mm/m) or one (1) percent, when first approved by the Administrative Authority.

6. Gravity Drainage Required

Wherever practicable, all plumbing fixtures shall be drained to the public sewer or private sewage disposal system by gravity.

7. Drainage of Fixtures Located Below the Next Upstream Manhole or Below the Main Sewer Level

7.1. A sewage ejector or sewage pump receiving the discharge of water closets or urinals:

In single dwelling units, the ejector or pump shall be capable of passing a   two (2) inches (51 mm) diameter solid ball, and the discharge piping of each ejector or pump shall have a backwater valve and gate valve, and be a minimum of three (3) inches (80 mm) in diameter.

7.2. Building drains or building sewers receiving discharge from any pump or ejector shall be adequately sized to prevent overloading. Two (2) fixture units shall be allowed for each gallon per minute (0.06 L/s) of flow.

Copyright © 2002 CONCORD ELECTRIC(HK)CO LTD. All Rights Reserved.